## Dashboard Prototype
Tag Name | Remote Start | Emergency_Mode | M_Gen_real_enrg | M_Total_Main_po | M_SLD_Gen_Brkr52GAux | M_SLD_Brkr52MAux | P&C Alarms
Modbus | 20523 | 20507 | 20680 | 20684 | 20692 | 20690
Output Tytpe | 0 = GREEN LIGHT 1 = RED LIGHT | 1 = GREEN LIGHT 0 = RED LIGHT |  |  | 0 = CLOSED (RED LIGHT WITH CLOSE) | 1= OPEN (GREEN) | *If MODBUS ADDRESSES 20613 to 20664 = 1 then Alarm Status = 1 else Alarm Status = 0; **Also if any of 20537, 20512, 20513, 20510, 20511 =1, then Alarm Status=1; 0= Green Light 1 = Red Light | Note:UREA LEVEL; There's an API script that we run every day that we can run in the server and get the value. ********* If Urea is under 51%, it should go red
Project | Generator Status | Emergency Start Initiated | Generator Power kW | Store Load kW | Generator Breaker (52G) Status | Main Breaker (52U) Status | P&C Alarm | UREA Level | Time
Whitby |  |  | 500 | 498 |  |  |  | 97% | 2018-07-09 14:21
………
*** Add chart to each site, display Generator Power graph.
*** On Top of Dashboard page, add
|  | 15 |  | 10 |  |  | 10000
Total Number of Projects
|  |  |  | Number of Running Generators |  |  | Total Generator Power
*** And add Chart of the Total Number of Running Generators, chart of the Total Generator Power.
Note on F4: Jerick: Change Modbus ID
Note on G4: Song, Weifeng X. -ND: Change Modbus ID
Note on F5: Song, Weifeng X. -ND: Change icons and logic
Note on G5: Song, Weifeng X. -ND: Change Icons and logic

## Project Details
Project Name | Whitby
Project Address | 200 Taunton Rd W
Project Size | 1000
Store Number | 1058
Operation Mode | Closed Transition
Description | Utility Main | Generator
Total Power, kW | 20684 | 20680 |  | Tag Taken from RTAC
Average Current, A | 20676 | 20678 |  | Tag Taken from RTAC
Average Voltage, V | 20670 | 20664 |  | Tag Taken from RTAC
Power Factor, pF | 20668 | 20660 |  | Tag Taken from RTAC
Last Run's Real Energy, kWh
Yesterday's Real Energy, kWh
Month-To-Date Real Energy, kWh
Total Real Energy, kWh | - |  | Only for generator/This will just add the daily kWh production. GCS to provide the baseline value
Urea Level | N/A | 97%
Hours till Next Maintenance | N/A | 20546 | Word | This is taken from the Easygen Tag
Site Status
Generator Status
Main Breaker Status
Generator Breaker Status
Operation Mode: Parallel |  |  | if Operation Mode is "Closed Transition", just show "N/A" icon
Remote Start Initiated
86G Lockout |  |  | 20519
86U Lockout |  |  | 20520
Emergency Mode Initiated
RTAC Status
Utility Connect Permission
Utility Allow Connect
Utility Trip Disconnect Command
Utility Block Connect
EMCP_Status
Communication Devices Status |  |  | Modbus
SEL_Com_Status |  |  | 20842 (Word) | 0=GREEN
EZ_Com_Status |  |  | 20840 (Word) | 1=RED
ACMG_Com_Status |  |  | 20844 (Word)
Primary Modem State |  |  | 22413 | Byte | Normal = 7; Any value other than 7 is unmormal!
EMCP_Status |  |  | 20895 (Word)
ALARMS
Start Time | End Time | Descripton
Can we make the alarm Section to look like this below? With sliders?
Note on A46: astejada: Start Time is when the time when the Modbus becomes 1
Note on B46: astejada: End Time is when the time when the Modbus becomes 1
Note on C46: astejada: Insert Alarm Description from RTAC Alarms Tab

## Alarms
# | Trigger & Action | Notes
1 | *If MODBUS ADDRESSES 20613 to 20664 = 1 then P&C Alarm Status = 1 else P&C Alarm Status = 0; 0= Green Light 1 = Red Light
2 | **Also if any of 20537, 20512, 20513, 20510, 20511 =1, then P&C Alarm Status=1; 0= Green Light ; 1 = Red Light
3 | If Urea is under 51%, Dashboard UREA should go red
4 | If comm/datq received is more than 15 minutes, its Dashboard Time should turn red
5 | If Engin_Fault = 1, then P&C Alarm Status=1; 0= Green Light ; 1 = Red Light
*** | All Alarms show be recorded and displayed on Project Details page.

## MODBUS ADDRESS
Obvius POINT# | Obvius Modbus Function | Obvius Modbus Address | Modbus Address | Data Type | Tag Name | Description | Comments
0 | Read Coil | 20503 | 20503 | Bool | EZ_G_13 | The genset runs mains parallel
1 | Read Coil | 20507 | 20507 | Bool | Emergency_Mode
2 | Read Coil | 20508 | 20508 | Bool | Dig_Input_0 | Utility breaker status
3 | Read Coil | 20509 | 20509 | Bool | Dig_Input_1 | Gen breaker status
4 | Read Coil | 20510 | 20510 | Bool | RTAC_Trip | Trip command
5 | Read Coil | 20511 | 20511 | Bool | RTAC_Block | Block Command
6 | Read Coil | 20512 | 20512 | Bool | RTAC_Perm_Stat | Permission Status | NEW***
7 | Read Coil | 20513 | 20513 | Bool | RTAC_Allow | Allow Connection Permit
8 | Read Coil | 20519 | 20519 | Bool | M_86GLo_Tr | 86G Lock Out Trip
9 | Read Coil | 20520 | 20520 | Bool | M_86MLo_Tr | 86U Lock Out Trip | 86U or 86M are the same. Sometimes they use U for Utility or M for Main. These are the same breaker
82 | Read Coil | 20521 | 20521 | Bool | M_Brkr52GAux
83 | Read Coil | 20522 | 20522 | Bool | M_Brkr52MAux
10 | Read Coil | 20523 | 20523 | Bool | M_Start_Auto | Remote Start Initiated | Change this MODBUS TO 20523/ OLD WAS 20694
11 | Read Coil | 20537 | 20537 | Bool | M_Start_Inhibit
12 | Read Coil | 20613 | 20613 | Bool | SEL_D_1 | 50 PHASE
13 | Read Coil | 20614 | 20614 | Bool | SEL_D_2 | 50 GROUND
14 | Read Coil | 20615 | 20615 | Bool | SEL_D_3 | SEL LO TRIP: 50 NEGSEQ
15 | Read Coil | 20616 | 20616 | Bool | SEL_D_4 | SEL LO TRIP: 51 PHASE
16 | Read Coil | 20617 | 20617 | Bool | SEL_D_5 | SEL LO TRIP: 51 GROUND
17 | Read Coil | 20618 | 20618 | Bool | SEL_D_6 | SEL LO TRIP:51 NEGSEQ
18 | Read Coil | 20619 | 20619 | Bool | SEL_D_7 | SEL LO TRIP: NEUTRAL 50
19 | Read Coil | 20620 | 20620 | Bool | SEL_D_8 | SEL LO TRIP: NEUTRAL 51
20 | Read Coil | 20621 | 20621 | Bool | SEL_D_9 | SEL LO TRIP: 67 PHASE
21 | Read Coil | 20622 | 20622 | Bool | SEL_D_10 | SEL LO TRIP: 67 GROUND
22 | Read Coil | 20623 | 20623 | Bool | SEL_D_11 | SEL LO TRIP: 67 NEGSEQ
23 | Read Coil | 20624 | 20624 | Bool | SEL_D_12 | SEL LO TRIP: 46 NEGSEQ
24 | Read Coil | 20625 | 20625 | Bool | SEL_D_13 | SEL LO TRIP: 49T THERMAL
25 | Read Coil | 20626 | 20626 | Bool | SEL_D_14 | SEL LO TRIP: GND DIFF 87N
26 | Read Coil | 20627 | 20627 | Bool | SEL_D_15 | SEL LO TRIP: RESTR DIFF 87R
27 | Read Coil | 20628 | 20628 | Bool | SEL_D_16 | SEL LO TRIP: UNRSTR DIFF 87U
28 | Read Coil | 20629 | 20629 | Bool | SEL_DD_1 | SEL TRIP HI: UNDERVOLT 27P
29 | Read Coil | 20630 | 20630 | Bool | SEL_DD_2 | SEL TRIP HI: OVERVOLT 59P
30 | Read Coil | 20631 | 20631 | Bool | SEL_DD_3 | RESERVED
31 | Read Coil | 20632 | 20632 | Bool | SEL_DD_4 | SEL TRIP HI: POWER ELEMENTS
32 | Read Coil | 20633 | 20633 | Bool | SEL_DD_5 | SEL TRIP HI: FREQUENCY 81
33 | Read Coil | 20634 | 20634 | Bool | SEL_DD_6 | SEL TRIP HI: VOLTS/HERTZ
34 | Read Coil | 20635 | 20635 | Bool | SEL_DD_7 | SEL TRIP HI: RESTRCTD EARTH
35 | Read Coil | 20636 | 20636 | Bool | SEL_DD_8 | SEL TRIP HI: RTD TRIP
36 | Read Coil | 20637 | 20637 | Bool | SEL_DD_9 | SEL TRIP HI: BREAKER FAIL
37 | Read Coil | 20638 | 20638 | Bool | SEL_DD_10 | SEL TRIP HI: REMOTE TRIP
38 | Read Coil | 20639 | 20639 | Bool | SEL_DD_11 | BACKUP
39 | Read Coil | 20640 | 20640 | Bool | SEL_DD_12 | SEL TRIP HI: 40 FLD LOSS
40 | Read Coil | 20641 | 20641 | Bool | SEL_DD_13 | SEL TRIP HI: 64G/64F GND
41 | Read Coil | 20642 | 20642 | Bool | SEL_DD_14 | SEL TRIP HI: INADVERTENT ENRG
42 | Read Coil | 20643 | 20643 | Bool | SEL_DD_15 | SEL TRIP HI: OUT OF STEP
43 | Read Coil | 20644 | 20644 | Bool | SEL_DD_16 | SEL TRIP HI: TRIP
44 | Read Coil | 20645 | 20645 | Bool | SEL_DDD_1 | SEL WARNING LO: BREAKER MONITOR
45 | Read Coil | 20646 | 20646 | Bool | SEL_DDD_2 | SEL WARNING LO: DEMAND ALARM
46 | Read Coil | 20647 | 20647 | Bool | SEL_DDD_3 | SEL WARNING LO: RTD FAULT
47 | Read Coil | 20648 | 20648 | Bool | SEL_DDD_4 | CONFIG FAULT
48 | Read Coil | 20649 | 20649 | Bool | SEL_DDD_5 | COMM FAULT
49 | Read Coil | 20650 | 20650 | Bool | SEL_DDD_6 | COMM IDLE
50 | Read Coil | 20651 | 20651 | Bool | SEL_DDD_7 | COMM LOSS
51 | Read Coil | 20652 | 20652 | Bool | SEL_DDD_8 | SEL WARNING LO: DIFF ALARM 87A
52 | Read Coil | 20653 | 20653 | Bool | SEL_DDD_9 | SEL WARNING LO: 5TH HARMONIC
53 | Read Coil | 20654 | 20654 | Bool | SEL_DDD_10 | SEL WARNING LO: RTD ALARM
54 | Read Coil | 20655 | 20655 | Bool | SEL_DDD_11 | SEL WARNING LO: LOSS OF POTENTIAL
55 | Read Coil | 20656 | 20656 | Bool | SEL_DDD_12 | SEL WARNING LO: AI HI/LO ALARM
56 | Read Coil | 20657 | 20657 | Bool | SEL_DDD_13 | SEL WARNING LO: 49A THERMAL ALARM
57 | Read Coil | 20658 | 20658 | Bool | SEL_DDD_14 | SEL WARNING LO: HALARM
58 | Read Coil | 20659 | 20659 | Bool | SEL_DDD_15 | SEL WARNING LO: SALARM
59 | Read Coil | 20660 | 20660 | Bool | SEL_DDD_16 | SEL WARNING LO: WARNING
60 | Read Coil | 20661 | 20661 | Bool | SEL_D4_1 | SEL WARNING HI: UNDERVOLT 27P
61 | Read Coil | 20662 | 20662 | Bool | SEL_D4_2 | SEL WARNING HI: OVERVOLT 59P
62 | Read Coil | 20663 | 20663 | Bool | SEL_D4_3 | SEL WARNING HI: 46 NEGSEQ
63 | Read Coil | 20664 | 20664 | Bool | SEL_D4_4 | VOLTS/HERTZ
64 | Read Holding Registers | 420039 | 20038 | Float | S_Gen_real_enrg | Gen. real energy | Alternative is modbus 20680 *** / Maybe good to put get this data as well.
65 | Read Holding Registers | 420533 | 20532 | Word | Total_Gen_Power | Generator Power (kW)
66 | Read Holding Registers | 420536 | 20535 | Int | Total_mains_pow | Store Load (kW)
67 | Read Holding Registers | 420547 | 20546 | Word | Hrs_until_maint | Hours until next maintenance
68 | Read Holding Registers | 420548 | 20547 | Word | Gen_Hrs | Gen. hours of operation * * * Scale Req * …
69 | Read Holding Registers | 420661 | 20660 | Float | M_Gen_Power_fac | Power Factor
70 | Read Holding Registers | 420665 | 20664 | Float | M_Av_Gen_DeltaV | Volts
71 | Read Holding Registers | 420669 | 20668 | Float | M_Main_power_pf | Power Factor
72 | Read Holding Registers | 420671 | 20670 | Float | M_Av_Main_Del_V | Volts
73 | Read Holding Registers | 420677 | 20676 | Float | M_Av_Main_Curnt | Amps (Current)
74 | Read Holding Registers | 420679 | 20678 | Float | M_Av_Gen_Crnt | Amps (Current)
75 | Read Holding Registers | 420681 | 20680 | Float | M_Gen_real_enrg | Kilo-Watt
76 | Read Holding Registers | 420685 | 20684 | Float | M_Total_Main_po | Kilo-Watt
77 | Read Holding Registers | 420841 | 20840 | Word | EZ_Com_Status | EZ_Com_Status
78 | Read Holding Registers | 420843 | 20842 | Word | SEL_Com_Status | SEL_Com_Status
79 | Read Holding Registers | 420845 | 20844 | Word | ACMG_Com_Status | ACMG_Com_Status
80 | Read Holding Registers | 420896 | 20895 | Word | EMCP_Status | EMCP_Status
81 | Read Holding Registers | 421027 | 21026 | Word | Genset_Status | Generator Run Status
84 | Read Holding Registers | 422414 | 22413 | Byte | COM4_ModemState | Modem state | Normal = 7; Any value other than 7 is unmormal!
85 | Read Coil | 20547 | 20547 | Bool | Engin_Fault | Engine Fault | 0 = Normal; 1 = Fault
86 | Read Holding Registers | 420691 | 20690 | Float | M_SLD_Brkr52MAux | Main Breaker Status | 0 = Close; 1 = Open
87 | Read Holding Registers | 420693 | 20692 | Float | M_SLD_Gen_Brkr52GAux | Generator Breaker Status | 0 = Close; 1 = Open

## Project Info
Project Number | Fund Name | Project Size, kW | Site Name | Address | Store Number | Operation Mode | Primary IP (Bell) | Backup Rogers IP
152854 | TPG | 1000 | Aurora | 15900 Bayview Ave | 1030 | Closed Transition | 174.90.154.17 | 74.198.124.222
152855 | TPG | 1000 | Richmond Hill | 301 Hightech Rd | 1028 | Paralleling | 174.90.154.18 | 74.198.115.159
152853 | TPG | 1000 | Markham | 200 Bullock Ave | 1032 | Paralleling | 174.90.154.15 | 74.198.115.156
152852 | TPG | 1000 | Newmarket | 18120 Yonge St | 1018 | Closed Transition | 174.90.154.6 | 74.198.115.155
152857 | TPG | 1000 | Glen Erin | 5010 Glen Erin Dr | 1011 | Closed Transition | 174.90.154.7 | 74.198.115.163
152850 | TPG | 1000 | Winston Churchill | 3050 Argentia Rd | 1080 | Closed Transition | 174.90.154.8 | 74.198.115.160
152849 | TPG | 1000 | North Oakville | 201 Oak Park | 1024 | Paralleling | 174.90.154.14 | 74.198.115.161
152871 | TPG | 1000 | South Orleans | 4270 Innes Rd | 1071 | Closed Transition | 174.90.154.61 | 74.198.115.162
152865 | TPG | 1000 | Oshawa | 1385 Harmony Rd | 1043 | Closed Transition | 174.90.154.60 | 74.198.115.154
152864 | TPG | 1000 | Milton | 820 Main St | 2810 | Closed Transition | 174.90.154.62 | 74.198.115.157
152856 | TPG | 1000 | Kitchener | 875 Highland Rd | 2822 | Closed Transition | 174.90.154.59 | 74.198.115.158
152866 | TPG | 1000 | Whitby | 200 Taunton Rd W | 1058 | Closed Transition | 174.90.154.63 | 74.198.115.152
| TPG | 1000 | Dufferin | 51 Gerry Fitzgerald | 1033 | Closed Transition | 174.90.154.225 | 74.198.124.38
| TPG | 1000 | Walker | 4371 Walkers RD | 567 | Closed Transition | 174.90.154.226 | 74.198.124.37
| TPG | 1000 | Don Mills | 825 Don Mills | 1077 | Closed Transition | 174.90.154.227 | 74.198.124.64
| TPG | 1000 | Brimley | 1755 Brimley | 2809 | Closed Transition | 174.90.154.228 | 74.198.124.63
| TPG | 1000 | Weston | 2549 Weston Rd | 2800 | Closed Transition | 174.90.154.229 | 74.198.124.40
Moving forward, we do not need to know if it is closed or open Transition (Operation Mode). All stores will be transferred over to Closed Transition once we get all the approval from the Ministry.