## Dashboard Prototype
Tag Name | Remote Start | Emergency_Mode | M_Gen_real_enrg | M_Total_Main_po | M_SLD_Gen_Brkr52GAux | M_SLD_Brkr52MAux | P&C Alarms
Modbus | 20523 | 20507 | 20680 | 20684 | 20692 | 20690
Output Tytpe | 0 = GREEN LIGHT 1 = RED LIGHT | 1 = GREEN LIGHT 0 = RED LIGHT |  |  | 0 = CLOSED (RED LIGHT WITH CLOSE) | 1= OPEN (GREEN) | *If MODBUS ADDRESSES 20613 to 20664 = 1 then Alarm Status = 1 else Alarm Status = 0; **Also if any of 20537, 20512, 20513, 20510, 20511 =1, then Alarm Status=1; 0= Green Light 1 = Red Light | Note:UREA LEVEL; There's an API script that we run every day that we can run in the server and get the value. ********* If Urea is under 51%, it should go red
Project | Generator Status | Emergency Start Initiated | Generator Power kW | Store Load kW | Generator Breaker (52G) Status | Main Breaker (52U) Status | P&C Alarm | UREA Level | Time
Whitby |  |  | 500 | 498 |  |  |  | 97% | 2018-07-09 14:21
………
*** Add chart to each site, display Generator Power graph.
*** On Top of Dashboard page, add
|  | 15 |  | 10 |  |  | 10000
Total Number of Projects
|  |  |  | Number of Running Generators |  |  | Total Generator Power
*** And add Chart of the Total Number of Running Generators, chart of the Total Generator Power.
Note on F4: Jerick: Change Modbus ID
Note on G4: Song, Weifeng X. -ND: Change Modbus ID
Note on F5: Song, Weifeng X. -ND: Change icons and logic
Note on G5: Song, Weifeng X. -ND: Change Icons and logic

## Project Details
Project Name | Whitby
Project Address | 200 Taunton Rd W
Project Size | 1000
Store Number | 1058
Operation Mode | Closed Transition
Description | Utility Main | Generator
Total Power, kW | 20684 | 20680 |  | Tag Taken from RTAC
Average Current, A | 20676 | 20678 |  | Tag Taken from RTAC
Average Voltage, V | 20670 | 20664 |  | Tag Taken from RTAC
Power Factor, pF | 20668 | 20660 |  | Tag Taken from RTAC
Last Run's Real Energy, kWh
Yesterday's Real Energy, kWh
Month-To-Date Real Energy, kWh
Total Real Energy, kWh | - |  | Only for generator/This will just add the daily kWh production. GCS to provide the baseline value
Urea Level | N/A | 97%
Hours till Next Maintenance | N/A | 20546 | Word | This is taken from the Easygen Tag
Site Status
Generator Status
Main Breaker Status
Generator Breaker Status
Operation Mode: Parallel |  |  | if Operation Mode is "Closed Transition", just show "N/A" icon
Remote Start Initiated
86G Lockout |  |  | 20519
86U Lockout |  |  | 20520
Emergency Mode Initiated
RTAC Status
Utility Connect Permission
Utility Allow Connect
Utility Trip Disconnect Command
Utility Block Connect
EMCP_Status
Communication Devices Status |  |  | Modbus
SEL_Com_Status |  |  | 20842 (Word) | 0=GREEN
EZ_Com_Status |  |  | 20840 (Word) | 1=RED
ACMG_Com_Status |  |  | 20844 (Word)
Primary Modem State |  |  | 22413 | Byte | Normal = 7; Any value other than 7 is unmormal!
EMCP_Status |  |  | 20895 (Word)
ALARMS
Start Time | End Time | Descripton
Can we make the alarm Section to look like this below? With sliders?
Note on A46: astejada: Start Time is when the time when the Modbus becomes 1
Note on B46: astejada: End Time is when the time when the Modbus becomes 1
Note on C46: astejada: Insert Alarm Description from RTAC Alarms Tab

## Alarms
# | Trigger & Action | Notes
1 | *If MODBUS ADDRESSES 20613 to 20664 = 1 then P&C Alarm Status = 1 else P&C Alarm Status = 0; 0= Green Light 1 = Red Light
2 | **Also if any of 20537, 20512, 20513, 20510, 20511 =1, then P&C Alarm Status=1; 0= Green Light ; 1 = Red Light
3 | If Urea is under 51%, Dashboard UREA should go red
4 | If comm/datq received is more than 15 minutes, its Dashboard Time should turn red
5 | If Engin_Fault = 1, then P&C Alarm Status=1; 0= Green Light ; 1 = Red Light
*** | All Alarms show be recorded and displayed on Project Details page.

## MODBUS ADDRESS
Obvius POINT# | Obvius Modbus Function | Obvius Modbus Address | Modbus Address | Data Type | Tag Name | Description | Comments
0 | Read Coil | 20503 | 20503 | Bool | EZ_G_13 | The genset runs mains parallel
1 | Read Coil | 20507 | 20507 | Bool | Emergency_Mode
2 | Read Coil | 20508 | 20508 | Bool | Dig_Input_0 | Utility breaker status
3 | Read Coil | 20509 | 20509 | Bool | Dig_Input_1 | Gen breaker status
4 | Read Coil | 20510 | 20510 | Bool | RTAC_Trip | Trip command
5 | Read Coil | 20511 | 20511 | Bool | RTAC_Block | Block Command
6 | Read Coil | 20512 | 20512 | Bool | RTAC_Perm_Stat | Permission Status | NEW***
7 | Read Coil | 20513 | 20513 | Bool | RTAC_Allow | Allow Connection Permit
8 | Read Coil | 20519 | 20519 | Bool | M_86GLo_Tr | 86G Lock Out Trip
9 | Read Coil | 20520 | 20520 | Bool | M_86MLo_Tr | 86U Lock Out Trip | 86U or 86M are the same. Sometimes they use U for Utility or M for Main. These are the same breaker
82 | Read Coil | 20521 | 20521 | Bool | M_Brkr52GAux
83 | Read Coil | 20522 | 20522 | Bool | M_Brkr52MAux
10 | Read Coil | 20523 | 20523 | Bool | M_Start_Auto | Remote Start Initiated | Change this MODBUS TO 20523/ OLD WAS 20694
11 | Read Coil | 20537 | 20537 | Bool | M_Start_Inhibit
12 | Read Coil | 20613 | 20613 | Bool | SEL_D_1 | 50 PHASE
13 | Read Coil | 20614 | 20614 | Bool | SEL_D_2 | 50 GROUND
14 | Read Coil | 20615 | 20615 | Bool | SEL_D_3 | SEL LO TRIP: 50 NEGSEQ
15 | Read Coil | 20616 | 20616 | Bool | SEL_D_4 | SEL LO TRIP: 51 PHASE
16 | Read Coil | 20617 | 20617 | Bool | SEL_D_5 | SEL LO TRIP: 51 GROUND
17 | Read Coil | 20618 | 20618 | Bool | SEL_D_6 | SEL LO TRIP:51 NEGSEQ
18 | Read Coil | 20619 | 20619 | Bool | SEL_D_7 | SEL LO TRIP: NEUTRAL 50
19 | Read Coil | 20620 | 20620 | Bool | SEL_D_8 | SEL LO TRIP: NEUTRAL 51
20 | Read Coil | 20621 | 20621 | Bool | SEL_D_9 | SEL LO TRIP: 67 PHASE
21 | Read Coil | 20622 | 20622 | Bool | SEL_D_10 | SEL LO TRIP: 67 GROUND
22 | Read Coil | 20623 | 20623 | Bool | SEL_D_11 | SEL LO TRIP: 67 NEGSEQ
23 | Read Coil | 20624 | 20624 | Bool | SEL_D_12 | SEL LO TRIP: 46 NEGSEQ
24 | Read Coil | 20625 | 20625 | Bool | SEL_D_13 | SEL LO TRIP: 49T THERMAL
25 | Read Coil | 20626 | 20626 | Bool | SEL_D_14 | SEL LO TRIP: GND DIFF 87N
26 | Read Coil | 20627 | 20627 | Bool | SEL_D_15 | SEL LO TRIP: RESTR DIFF 87R
27 | Read Coil | 20628 | 20628 | Bool | SEL_D_16 | SEL LO TRIP: UNRSTR DIFF 87U
28 | Read Coil | 20629 | 20629 | Bool | SEL_DD_1 | SEL TRIP HI: UNDERVOLT 27P
29 | Read Coil | 20630 | 20630 | Bool | SEL_DD_2 | SEL TRIP HI: OVERVOLT 59P
30 | Read Coil | 20631 | 20631 | Bool | SEL_DD_3 | RESERVED
31 | Read Coil | 20632 | 20632 | Bool | SEL_DD_4 | SEL TRIP HI: POWER ELEMENTS
32 | Read Coil | 20633 | 20633 | Bool | SEL_DD_5 | SEL TRIP HI: FREQUENCY 81
33 | Read Coil | 20634 | 20634 | Bool | SEL_DD_6 | SEL TRIP HI: VOLTS/HERTZ
34 | Read Coil | 20635 | 20635 | Bool | SEL_DD_7 | SEL TRIP HI: RESTRCTD EARTH
35 | Read Coil | 20636 | 20636 | Bool | SEL_DD_8 | SEL TRIP HI: RTD TRIP
36 | Read Coil | 20637 | 20637 | Bool | SEL_DD_9 | SEL TRIP HI: BREAKER FAIL
37 | Read Coil | 20638 | 20638 | Bool | SEL_DD_10 | SEL TRIP HI: REMOTE TRIP
38 | Read Coil | 20639 | 20639 | Bool | SEL_DD_11 | BACKUP
39 | Read Coil | 20640 | 20640 | Bool | SEL_DD_12 | SEL TRIP HI: 40 FLD LOSS
40 | Read Coil | 20641 | 20641 | Bool | SEL_DD_13 | SEL TRIP HI: 64G/64F GND
41 | Read Coil | 20642 | 20642 | Bool | SEL_DD_14 | SEL TRIP HI: INADVERTENT ENRG
42 | Read Coil | 20643 | 20643 | Bool | SEL_DD_15 | SEL TRIP HI: OUT OF STEP
43 | Read Coil | 20644 | 20644 | Bool | SEL_DD_16 | SEL TRIP HI: TRIP
44 | Read Coil | 20645 | 20645 | Bool | SEL_DDD_1 | SEL WARNING LO: BREAKER MONITOR
45 | Read Coil | 20646 | 20646 | Bool | SEL_DDD_2 | SEL WARNING LO: DEMAND ALARM
46 | Read Coil | 20647 | 20647 | Bool | SEL_DDD_3 | SEL WARNING LO: RTD FAULT
47 | Read Coil | 20648 | 20648 | Bool | SEL_DDD_4 | CONFIG FAULT
48 | Read Coil | 20649 | 20649 | Bool | SEL_DDD_5 | COMM FAULT
49 | Read Coil | 20650 | 20650 | Bool | SEL_DDD_6 | COMM IDLE
50 | Read Coil | 20651 | 20651 | Bool | SEL_DDD_7 | COMM LOSS
51 | Read Coil | 20652 | 20652 | Bool | SEL_DDD_8 | SEL WARNING LO: DIFF ALARM 87A
52 | Read Coil | 20653 | 20653 | Bool | SEL_DDD_9 | SEL WARNING LO: 5TH HARMONIC
53 | Read Coil | 20654 | 20654 | Bool | SEL_DDD_10 | SEL WARNING LO: RTD ALARM
54 | Read Coil | 20655 | 20655 | Bool | SEL_DDD_11 | SEL WARNING LO: LOSS OF POTENTIAL
55 | Read Coil | 20656 | 20656 | Bool | SEL_DDD_12 | SEL WARNING LO: AI HI/LO ALARM
56 | Read Coil | 20657 | 20657 | Bool | SEL_DDD_13 | SEL WARNING LO: 49A THERMAL ALARM
57 | Read Coil | 20658 | 20658 | Bool | SEL_DDD_14 | SEL WARNING LO: HALARM
58 | Read Coil | 20659 | 20659 | Bool | SEL_DDD_15 | SEL WARNING LO: SALARM
59 | Read Coil | 20660 | 20660 | Bool | SEL_DDD_16 | SEL WARNING LO: WARNING
60 | Read Coil | 20661 | 20661 | Bool | SEL_D4_1 | SEL WARNING HI: UNDERVOLT 27P
61 | Read Coil | 20662 | 20662 | Bool | SEL_D4_2 | SEL WARNING HI: OVERVOLT 59P
62 | Read Coil | 20663 | 20663 | Bool | SEL_D4_3 | SEL WARNING HI: 46 NEGSEQ
63 | Read Coil | 20664 | 20664 | Bool | SEL_D4_4 | VOLTS/HERTZ
64 | Read Holding Registers | 420039 | 20038 | Float | S_Gen_real_enrg | Gen. real energy | Alternative is modbus 20680 *** / Maybe good to put get this data as well.
65 | Read Holding Registers | 420533 | 20532 | Word | Total_Gen_Power | Generator Power (kW)
66 | Read Holding Registers | 420536 | 20535 | Int | Total_mains_pow | Store Load (kW)
67 | Read Holding Registers | 420547 | 20546 | Word | Hrs_until_maint | Hours until next maintenance
68 | Read Holding Registers | 420548 | 20547 | Word | Gen_Hrs | Gen. hours of operation * * * Scale Req * …
69 | Read Holding Registers | 420661 | 20660 | Float | M_Gen_Power_fac | Power Factor
70 | Read Holding Registers | 420665 | 20664 | Float | M_Av_Gen_DeltaV | Volts
71 | Read Holding Registers | 420669 | 20668 | Float | M_Main_power_pf | Power Factor
72 | Read Holding Registers | 420671 | 20670 | Float | M_Av_Main_Del_V | Volts
73 | Read Holding Registers | 420677 | 20676 | Float | M_Av_Main_Curnt | Amps (Current)
74 | Read Holding Registers | 420679 | 20678 | Float | M_Av_Gen_Crnt | Amps (Current)
75 | Read Holding Registers | 420681 | 20680 | Float | M_Gen_real_enrg | Kilo-Watt
76 | Read Holding Registers | 420685 | 20684 | Float | M_Total_Main_po | Kilo-Watt
77 | Read Holding Registers | 420841 | 20840 | Word | EZ_Com_Status | EZ_Com_Status
78 | Read Holding Registers | 420843 | 20842 | Word | SEL_Com_Status | SEL_Com_Status
79 | Read Holding Registers | 420845 | 20844 | Word | ACMG_Com_Status | ACMG_Com_Status
80 | Read Holding Registers | 420896 | 20895 | Word | EMCP_Status | EMCP_Status
81 | Read Holding Registers | 421027 | 21026 | Word | Genset_Status | Generator Run Status
84 | Read Holding Registers | 422414 | 22413 | Byte | COM4_ModemState | Modem state | Normal = 7; Any value other than 7 is unmormal!
85 | Read Coil | 20547 | 20547 | Bool | Engin_Fault | Engine Fault | 0 = Normal; 1 = Fault
86 | Read Holding Registers | 420691 | 20690 | Float | M_SLD_Brkr52MAux | Main Breaker Status | 0 = Close; 1 = Open
87 | Read Holding Registers | 420693 | 20692 | Float | M_SLD_Gen_Brkr52GAux | Generator Breaker Status | 0 = Close; 1 = Open

## Project Info
Project Number | Fund Name | Project Size, kW | Site Name | Address | Store Number | Operation Mode | Primary IP (Bell) | Backup Rogers IP
152854 | TPG | 1000 | Aurora | 15900 Bayview Ave | 1030 | Closed Transition | 174.90.154.17 | 74.198.124.222
152855 | TPG | 1000 | Richmond Hill | 301 Hightech Rd | 1028 | Paralleling | 174.90.154.18 | 74.198.115.159
152853 | TPG | 1000 | Markham | 200 Bullock Ave | 1032 | Paralleling | 174.90.154.15 | 74.198.115.156
152852 | TPG | 1000 | Newmarket | 18120 Yonge St | 1018 | Closed Transition | 174.90.154.6 | 74.198.115.155
152857 | TPG | 1000 | Glen Erin | 5010 Glen Erin Dr | 1011 | Closed Transition | 174.90.154.7 | 74.198.115.163
152850 | TPG | 1000 | Winston Churchill | 3050 Argentia Rd | 1080 | Closed Transition | 174.90.154.8 | 74.198.115.160
152849 | TPG | 1000 | North Oakville | 201 Oak Park | 1024 | Paralleling | 174.90.154.14 | 74.198.115.161
152871 | TPG | 1000 | South Orleans | 4270 Innes Rd | 1071 | Closed Transition | 174.90.154.61 | 74.198.115.162
152865 | TPG | 1000 | Oshawa | 1385 Harmony Rd | 1043 | Closed Transition | 174.90.154.60 | 74.198.115.154
152864 | TPG | 1000 | Milton | 820 Main St | 2810 | Closed Transition | 174.90.154.62 | 74.198.115.157
152856 | TPG | 1000 | Kitchener | 875 Highland Rd | 2822 | Closed Transition | 174.90.154.59 | 74.198.115.158
152866 | TPG | 1000 | Whitby | 200 Taunton Rd W | 1058 | Closed Transition | 174.90.154.63 | 74.198.115.152
|  |  | Dufferin | 51 Gerry Fitzgerald |  |  |  | 74.198.124.38
|  |  | Walker | 4371 Walkers RD |  |  |  | 74.198.124.37
|  |  | Don Mills | 825 Don Mills |  |  |  | 74.198.124.64
|  |  | Brimley | 1755 Brimley |  |  |  | 74.198.124.63
|  |  | Weston |  |  |  |  | 74.198.124.40