## Dashboard Prototype
Tag Name | Remote Start | Emergency_Mode | M_Gen_real_enrg | M_Total_Main_po | M_SLD_Gen_Brkr52GAux | M_SLD_Brkr52MAux | P&C Alarms
Modbus | 20523 | 20507 | 20680 | 20684 | 20692 | 20690
Output Tytpe | 0 = GREEN LIGHT 1 = RED LIGHT | 1 = GREEN LIGHT 0 = RED LIGHT |  |  | 0 = CLOSED (RED LIGHT WITH CLOSE) | 1= OPEN (GREEN) | *If MODBUS ADDRESSES 20613 to 20664 = 1 then Alarm Status = 1 else Alarm Status = 0; **Also if any of 20537, 20512, 20513, 20510, 20511 =1, then Alarm Status=1; 0= Green Light 1 = Red Light | Note:UREA LEVEL; There's an API script that we run every day that we can run in the server and get the value. ********* If Urea is under 51%, it should go red
Project | Generator Status | Emergency Start Initiated | Generator Power kW | Store Load kW | Generator Breaker (52G) Status | Main Breaker (52U) Status | P&C Alarm | UREA Level | Time
Whitby |  |  | 500 | 498 |  |  |  | 97% | 2018-07-09 14:21
………
*** Add chart to each site, display Generator Power graph.
*** On Top of Dashboard page, add
|  | 15 |  | 10 |  |  | 10000
Total Number of Projects
|  |  |  | Number of Running Generators |  |  | Total Generator Power
*** And add Chart of the Total Number of Running Generators, chart of the Total Generator Power.
Note on F4: Jerick: Change Modbus ID
Note on G4: Song, Weifeng X. -ND: Change Modbus ID
Note on F5: Song, Weifeng X. -ND: Change icons and logic
Note on G5: Song, Weifeng X. -ND: Change Icons and logic

## Project Details
Project Name | Whitby
Project Address | 200 Taunton Rd W
Project Size | 1000
Store Number | 1058
Description | Utility Main | Generator
Total Power, kW | 20684 | 20680 |  | Tag Taken from RTAC
Average Current, A | 20676 | 20678 |  | Tag Taken from RTAC
Average Voltage, V | 20670 | 20664 |  | Tag Taken from RTAC
Power Factor, pF | 20668 | 20660 |  | Tag Taken from RTAC
Last Run's Real Energy, kWh
Yesterday's Real Energy, kWh
Month-To-Date Real Energy, kWh
Total Real Energy, kWh | - |  | Only for generator/This will just add the daily kWh production. GCS to provide the baseline value
Urea Level | N/A | 97%
Hours till Next Maintenance | N/A | 20546 | Word | This is taken from the Easygen Tag
Site Status
Generator Status
Main Breaker Status
Generator Breaker Status
Remote Start Initiated
Engine Status |  |  | Tag name: Engin_Fault (20547); (0=Green/1=Red)
Emergency Start Initiated |  |  | Tag name: Emergency_Mode (20507)
Lockout Status
86G Lockout |  |  | Tag name: M_86GLo_Tr (20519) ; please reverse the logic (0=Green; 1=Red light)
86U Lockout |  |  | Tag name: M_86MLo_Tr (20520); please reverse the logic (0=Green; 1=Red light)
Start Inhibit Status
Utility Permission
Utility Connect Permission
Utility Allow Connect
Utility Trip Disconnect Command
Utility Block Connect
Communication Devices Status
SEL_Com_Status |  |  | 20842 (Word) | 1. Please reverse the logic of SEL_COM_STATUS; 1=GREEN; 0=RED?
EZ_Com_Status |  |  | 20840 (Word)
ACMG_Com_Status |  |  | 20844 (Word) | 0=GREEN
Primary Modem State |  |  | 22413 | 1=RED
EMCP_Status |  |  | 20895 (Word)
ALARMS
Start Time | End Time | Descripton | Please Change Time stamp to match dashboard (EST)
Can we make the alarm Section to look like this below? With sliders?
Note on A47: astejada: Start Time is when the time when the Modbus becomes 1
Note on B47: astejada: End Time is when the time when the Modbus becomes 1
Note on C47: astejada: Insert Alarm Description from RTAC Alarms Tab

## Alarms
# | Trigger & Action | Notes
1 | *If MODBUS ADDRESSES 20613 to 20664 = 1 then P&C Alarm Status = 1 else P&C Alarm Status = 0; 0= Green Light 1 = Red Light
2 | **Also if any of 20537, 20512, 20513, 20510, 20511 =1, then P&C Alarm Status=1; 0= Green Light ; 1 = Red Light
3 | If Urea is under 51%, Dashboard UREA should go red
4 | If comm/datq received is more than 15 minutes, its Dashboard Time should turn red
5 | If Engin_Fault = 1, then P&C Alarm Status=1; 0= Green Light ; 1 = Red Light
*** | All Alarms show be recorded and displayed on Project Details page.

## MODBUS ADDRESS
Obvius POINT# | Modbus Address | Data Type | Tag Name | Description | Comments
0 | 20503 | Bool | EZ_G_13 | The genset runs mains parallel
1 | 20507 | Bool | Emergency_Mode
2 | 20508 | Bool | Dig_Input_0 | Utility breaker status
3 | 20509 | Bool | Dig_Input_1 | Gen breaker status
4 | 20510 | Bool | RTAC_Trip | Trip command
5 | 20511 | Bool | RTAC_Block | Block Command
6 | 20512 | Bool | RTAC_Perm_Stat | Permission Status | NEW***
7 | 20513 | Bool | RTAC_Allow | Allow Connection Permit
8 | 20519 | Bool | M_86GLo_Tr | 86G Lock Out Trip
9 | 20520 | Bool | M_86MLo_Tr | 86U Lock Out Trip | 86U or 86M are the same. Sometimes they use U for Utility or M for Main. These are the same breaker
82 | 20521 | Bool | M_Brkr52GAux
83 | 20522 | Bool | M_Brkr52MAux
10 | 20523 | Bool | M_Start_Auto | Remote Start Initiated | Change this MODBUS TO 20523/ OLD WAS 20694
11 | 20537 | Bool | M_Start_Inhibit
12 | 20613 | Bool | SEL_D_1 | 50 PHASE
13 | 20614 | Bool | SEL_D_2 | 50 GROUND
14 | 20615 | Bool | SEL_D_3 | SEL LO TRIP: 50 NEGSEQ
15 | 20616 | Bool | SEL_D_4 | SEL LO TRIP: 51 PHASE
16 | 20617 | Bool | SEL_D_5 | SEL LO TRIP: 51 GROUND
17 | 20618 | Bool | SEL_D_6 | SEL LO TRIP:51 NEGSEQ
18 | 20619 | Bool | SEL_D_7 | SEL LO TRIP: NEUTRAL 50
19 | 20620 | Bool | SEL_D_8 | SEL LO TRIP: NEUTRAL 51
20 | 20621 | Bool | SEL_D_9 | SEL LO TRIP: 67 PHASE
21 | 20622 | Bool | SEL_D_10 | SEL LO TRIP: 67 GROUND
22 | 20623 | Bool | SEL_D_11 | SEL LO TRIP: 67 NEGSEQ
23 | 20624 | Bool | SEL_D_12 | SEL LO TRIP: 46 NEGSEQ
24 | 20625 | Bool | SEL_D_13 | SEL LO TRIP: 49T THERMAL
25 | 20626 | Bool | SEL_D_14 | SEL LO TRIP: GND DIFF 87N
26 | 20627 | Bool | SEL_D_15 | SEL LO TRIP: RESTR DIFF 87R
27 | 20628 | Bool | SEL_D_16 | SEL LO TRIP: UNRSTR DIFF 87U
28 | 20629 | Bool | SEL_DD_1 | SEL TRIP HI: UNDERVOLT 27P
29 | 20630 | Bool | SEL_DD_2 | SEL TRIP HI: OVERVOLT 59P
30 | 20631 | Bool | SEL_DD_3 | RESERVED
31 | 20632 | Bool | SEL_DD_4 | SEL TRIP HI: POWER ELEMENTS
32 | 20633 | Bool | SEL_DD_5 | SEL TRIP HI: FREQUENCY 81
33 | 20634 | Bool | SEL_DD_6 | SEL TRIP HI: VOLTS/HERTZ
34 | 20635 | Bool | SEL_DD_7 | SEL TRIP HI: RESTRCTD EARTH
35 | 20636 | Bool | SEL_DD_8 | SEL TRIP HI: RTD TRIP
36 | 20637 | Bool | SEL_DD_9 | SEL TRIP HI: BREAKER FAIL
37 | 20638 | Bool | SEL_DD_10 | SEL TRIP HI: REMOTE TRIP
38 | 20639 | Bool | SEL_DD_11 | BACKUP
39 | 20640 | Bool | SEL_DD_12 | SEL TRIP HI: 40 FLD LOSS
40 | 20641 | Bool | SEL_DD_13 | SEL TRIP HI: 64G/64F GND
41 | 20642 | Bool | SEL_DD_14 | SEL TRIP HI: INADVERTENT ENRG
42 | 20643 | Bool | SEL_DD_15 | SEL TRIP HI: OUT OF STEP
43 | 20644 | Bool | SEL_DD_16 | SEL TRIP HI: TRIP
44 | 20645 | Bool | SEL_DDD_1 | SEL WARNING LO: BREAKER MONITOR
45 | 20646 | Bool | SEL_DDD_2 | SEL WARNING LO: DEMAND ALARM
46 | 20647 | Bool | SEL_DDD_3 | SEL WARNING LO: RTD FAULT
47 | 20648 | Bool | SEL_DDD_4 | CONFIG FAULT
48 | 20649 | Bool | SEL_DDD_5 | COMM FAULT
49 | 20650 | Bool | SEL_DDD_6 | COMM IDLE
50 | 20651 | Bool | SEL_DDD_7 | COMM LOSS
51 | 20652 | Bool | SEL_DDD_8 | SEL WARNING LO: DIFF ALARM 87A
52 | 20653 | Bool | SEL_DDD_9 | SEL WARNING LO: 5TH HARMONIC
53 | 20654 | Bool | SEL_DDD_10 | SEL WARNING LO: RTD ALARM
54 | 20655 | Bool | SEL_DDD_11 | SEL WARNING LO: LOSS OF POTENTIAL
55 | 20656 | Bool | SEL_DDD_12 | SEL WARNING LO: AI HI/LO ALARM
56 | 20657 | Bool | SEL_DDD_13 | SEL WARNING LO: 49A THERMAL ALARM
57 | 20658 | Bool | SEL_DDD_14 | SEL WARNING LO: HALARM
58 | 20659 | Bool | SEL_DDD_15 | SEL WARNING LO: SALARM
59 | 20660 | Bool | SEL_DDD_16 | SEL WARNING LO: WARNING
60 | 20661 | Bool | SEL_D4_1 | SEL WARNING HI: UNDERVOLT 27P
61 | 20662 | Bool | SEL_D4_2 | SEL WARNING HI: OVERVOLT 59P
62 | 20663 | Bool | SEL_D4_3 | SEL WARNING HI: 46 NEGSEQ
63 | 20664 | Bool | SEL_D4_4 | VOLTS/HERTZ
64 | 20038 | Float | S_Gen_real_enrg | Gen. real energy | Alternative is modbus 20680 *** / Maybe good to put get this data as well.
65 | 20532 | Word | Total_Gen_Power | Generator Power (kW)
66 | 20535 | Int | Total_mains_pow | Store Load (kW)
67 | 20546 | Word | Hrs_until_maint | Hours until next maintenance
68 | 20547 | Word | Gen_Hrs | Gen. hours of operation * * * Scale Req * …
69 | 20660 | Float | M_Gen_Power_fac | Power Factor
70 | 20664 | Float | M_Av_Gen_DeltaV | Volts
71 | 20668 | Float | M_Main_power_pf | Power Factor
72 | 20670 | Float | M_Av_Main_Del_V | Volts
73 | 20676 | Float | M_Av_Main_Curnt | Amps (Current)
74 | 20678 | Float | M_Av_Gen_Crnt | Amps (Current)
75 | 20680 | Float | M_Gen_real_enrg | Kilo-Watt
76 | 20684 | Float | M_Total_Main_po | Kilo-Watt
77 | 20840 | Word | EZ_Com_Status | EZ_Com_Status
78 | 20842 | Word | SEL_Com_Status | SEL_Com_Status
79 | 20844 | Word | ACMG_Com_Status | ACMG_Com_Status
80 | 20895 | Word | EMCP_Status | EMCP_Status
81 | 21026 | Word | Genset_Status | Generator Run Status
84 | 22413 | Byte | COM4_ModemState | Modem state | Normal = 7; Any value other than 7 is unmormal!
85 | 20547 | Bool | Engin_Fault | Engine Fault | 0 = Normal; 1 = Fault
86 | 20690 | Float | M_SLD_Brkr52MAux | Main Breaker Status | 0 = Close; 1 = Open
87 | 20692 | Float | M_SLD_Gen_Brkr52GAux | Generator Breaker Status | 0 = Close; 1 = Open

## Project Info
Project Number | Fund Name | Project Size, kW | Site Name | Address | Store Number | Operation Mode | Primary IP (Bell) | Backup Rogers IP
152854 | TPG | 1000 | Aurora | 15900 Bayview Ave | 1030 | Closed Transition | 174.90.154.17 | 74.198.124.222
152855 | TPG | 1000 | Richmond Hill | 301 Hightech Rd | 1028 | Paralleling | 174.90.154.18 | 74.198.115.159
152853 | TPG | 1000 | Markham | 200 Bullock Ave | 1032 | Paralleling | 174.90.154.15 | 74.198.115.156
152852 | TPG | 1000 | Newmarket | 18120 Yonge St | 1018 | Closed Transition | 174.90.154.6 | 74.198.115.155
152857 | TPG | 1000 | Glen Erin | 5010 Glen Erin Dr | 1011 | Closed Transition | 174.90.154.7 | 74.198.115.163
152850 | TPG | 1000 | Winston Churchill | 3050 Argentia Rd | 1080 | Closed Transition | 174.90.154.8 | 74.198.115.160
152849 | TPG | 1000 | North Oakville | 201 Oak Park | 1024 | Paralleling | 174.90.154.14 | 74.198.115.161
152871 | TPG | 1000 | South Orleans | 4270 Innes Rd | 1071 | Closed Transition | 174.90.154.61 | 74.198.115.162
152865 | TPG | 1000 | Oshawa | 1385 Harmony Rd | 1043 | Closed Transition | 174.90.154.60 | 74.198.115.154
152864 | TPG | 1000 | Milton | 820 Main St | 2810 | Closed Transition | 174.90.154.62 | 74.198.115.157
152856 | TPG | 1000 | Kitchener | 875 Highland Rd | 2822 | Closed Transition | 174.90.154.59 | 74.198.115.158
152866 | TPG | 1000 | Whitby | 200 Taunton Rd W | 1058 | Closed Transition | 174.90.154.63 | 74.198.115.152
| TPG | 1000 | Dufferin | 51 Gerry Fitzgerald | 1033 | Closed Transition | 174.90.154.225 | 74.198.124.38
| TPG | 1000 | Walker | 4371 Walkers RD | 567 | Closed Transition | 174.90.154.226 | 74.198.124.37
| TPG | 1000 | Don Mills | 825 Don Mills | 1077 | Closed Transition | 174.90.154.227 | 74.198.124.64
| TPG | 1000 | Brimley | 1755 Brimley | 2809 | Closed Transition | 174.90.154.228 | 74.198.124.63
| TPG | 1000 | Weston | 2549 Weston Rd | 2800 | Closed Transition | 174.90.154.229 | 74.198.124.40
Moving forward, we do not need to know if it is closed or open Transition (Operation Mode). All stores will be transferred over to Closed Transition once we get all the approval from the Ministry.